**Request for Information (RFI)**

Project Name: Renovate Oncology

Project #: 528A8-18-805

Solicitation#: 36C24218B0572

Tuesday, October 09, 2018

**Stratton** **VA Medical Center Response**

**Q1:** Please provide a balance detail for room A921, as referred to in statement of work 4a.

**A1: Provide a report containing the measured air flows from each of the diffusers in suite A921, indicating whether these air flows are exhaust, supply, or return air. A detail will not be provided.**

**Q2:** Can we paint from floor to new ceiling in lieu of existing deck (refer to drawing A-002)

**A2: No. Paint entire wall, from deck to deck.**

**Q3:** What are the relocated hood certification requirements (as referred in statement of work 4b)?

**A3: The contractor is required to hire a third-party hood certification company to verify that the hood is acceptable to the USP 800 and NSF 49 requirements. The 6’ hood shall be relocated and certified over the weekend and it shall be operational for Monday morning.**

**Q4:** Can we maintain a dumpster on site for the duration of demolition phases?

**A4: Dumpsters are acceptable. The contractor will have to coordinate the size and location of the dumpster with the VA during the kickoff meeting.**

**Q5:** The SOW for work in Temporary Facility (5b.) mentions a specification section 09 51 00 which is not found in the specifications provided. The Table of Contents was not provided for reference either. Could you please provide both documents?

**A5: Specification section 095100 is attached along with the TOC. The type of ceiling is specified on drawing A-002 in the reflected ceiling part plan. An updated copy of this drawing is attached showing the extent of the ceiling types.**